SECTION 08 33 23.13 – HIGH PERFORMANCE OVERHEAD COILING DOORS

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

- NOTE:  The Albany RR200 is recommended for either interior environments only

      - SUMMARY

        - Section Includes:

          - High performance overhead coiling fabric doors for interior environments.

        - Related Requirements:

          - Section 05 50 00 "Metal Fabrications" for miscellaneous steel supports.

          - Division 26 and 28 Sections for electrical connections including conduit and wiring for coiling door operators and access control devices.

      - REFERENCES

        - References: Refer to the version year adopted by the Authority Having Jurisdiction.

          - National Electrical Manufacture’s Association (NEMA)

          - Underwriters Laboratories (UL)

        - National Electrical Manufacture’s Association (NEMA)

          - Type 4 - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against access to hazardous parts.

        - Underwriters Laboratories (UL).

          - UL 508 Standard for Industrial Control Panels.

        - Door & Access Systems Manufacturers Association (DASMA)

      - DEFINITIONS

        - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to open the door.

        - Safety Device:  A device that detects the presence of an object or person within a zone where injury could occur and provides a signal to stop the movement of the door.

        - High Performance Door:  A powered door characterized by rolling or folding action that is designed to sustain heavy usage at relatively high speeds.

        - High Speed Door:  (subcategory of high performance doors)  A non-swinging door used primarily to facilitate vehicular access or material transportation, with a minimum opening rate of 32 inches per second and a minimum closing rate of 24 inches per second.

      - SUBMITTALS

        - Comply with Division 01 - Submittal Procedures.

        - Product Data:  For each type of high performance overhead coiling door and accessory.

          - Include construction details, material descriptions, dimensions of individual sub-assemblies (side frames, header, control panel, motor), profiles for slats, and finishes.

          - Include operating characteristics, electrical characteristics, and furnished accessories.

          - Include description of automatic closing device and testing and resetting instructions.

        - Shop Drawings:  For each installation and for special components not dimensioned or detailed in manufacturer's product data.

          - Include plans, elevations, sections, and mounting details.

          - Show locations of controls, locking devices, and other accessories.

          - Include diagrams for power, signal, and control wiring.

        - Samples for Initial Selection:  Manufacturer's finish charts showing full range of colors and textures available for units with factory-applied finishes.

        - Samples for Verification:  For each type of exposed finish on the following components, in manufacturer's standard sizes:

          - Curtain fabric.

        - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

          - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

        - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals Including a detailed parts list for high performance overhead coiling doors in quantity as required in Division 01, Closeout Submittals.

      - QUALITY ASSURANCE

        - Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.

        - Installer Qualifications:  Installers, trained by the primary product manufacturer, with a minimum 3 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

        - Source Limitations:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

      - PROJECT CONDITIONS

        - Field Measurements: Verify actual dimensions of openings by field measurements before fabrication and indicate on shop drawings.

        - Electrical:  Verify actual job site power (voltage, phase and Hertz).

        - Verify environmental condition extremes.

        - Verify door sequence of operations.

      - COORDINATION

        - Coordinate sizes and locations of door openings and framing as required for high performance overhead coiling doors.

        - Electrical System Roughing-in: Coordinate layout and installation of high performance overhead coiling doors with connections to building power and access control system as applicable.

          - Fused disconnect required for each individual door within five feet of respective door (not supplied by door manufacturer).

      - WARRANTY

        - General Warranty: Reference Division 01, General Requirements. Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

        - High Performance Overhead Coiling Doors shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

        - Special Product Warranty:  Manufacturer's warranty in which manufacturer agrees to repair or replace components which fail to perform as follows:

          - The following warranties are in effect when the MCC VectorControl™ (variable frequency) Control System is supplied:

            - 5-year / 1,000,000 Cycle Limited Warranty on Drive Motor and Gearbox.

            - 2-year / 300,000 Cycle Limited Warranty on all other Mechanical and Electrical Components.

          - Door Fabric limited warranties:

            - 27 oz/yd2 Vinyl fabric panels are warranted for one (1) year.

            - transparent (PVC) polyvinyl chloride materials and windows are warranted for one (1) year.

        - During the warranty period a factory-trained technician shall perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

- PRODUCTS

      - MANUFACTURER

        - Manufacturer:  ASSA ABLOY Entrance Systems, 975-A Old Norcross Road, Lawrenceville, GA 30046.  Toll Free 1-800-ALBANY1.  Web- www.albanydoors.us Contact- sales.us.albany@assaabloy.com

- NOTE:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”

        - [Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section, “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

        - [Substitutions:  Not Permitted.]

      - HIGH PERFORMANCE OVERHEAD COILING DOORS

- NOTE:  The Albany RR200 is recommended for interior environments only

        - Model:  Albany RR200 high-speed industrial door. (Basis of Design):

          - Overhead coiling door with fabric curtain.

          - Overhead motor and gearbox drive system.

          - Door side frames.

          - Control panel, activation devices, and safety sensor devices.

      - PERFORMANCE REQUIREMENTS

        - Opening Speed:

          - Albany RR200:  Door to operate at a variable speed up to 80 inches (2.0m) per second.

        - Closing Speed:

          - Albany RR200:  Door to operate at a variable speed up to 24 inches (0.6m) per second.

        - Operation Cycles:  Drive motor and gearbox capable of operating for not less than 1,000,000 cycles.  One operation cycle is complete when a door is opened from the closed position to the fully open position and returned to the closed position.

      - DOOR ASSEMBLY

        - Door Curtain Design:

          - Door Fabric:  27 oz/yd2 Vinyl fabric material free of horizontal or vertical bars and/or stiffeners; constructed of an appropriate weight and material thickness to mold to the shape of any object or person it may contact with little or no impact.

- NOTE:  Select the following if vision panels are required for the project.

          - [Vision Panels:  Polyvinyl chloride (PVC).]

            - [Full width 15 inch (400 mm) height transparent vision panel.]

            - [Full width 31 inch (800 mm) height transparent vision panel.]

            - [25 inch x 23 inch (640 mm x 580 mm) transparent windows.]

          - Wireless reversing edge shall extend the full width of the fabric curtain bottom edge, sufficient to detect lateral and bottom edge impact.

            - Upon lateral impact at any position in any direction of travel, the fabric curtain releases from side frames and the door operation is stopped. Controller must indicate problem encountered and instruct operator on what steps should be taken to fix the problem.  Fabric curtain must be self-repairing. Door must automatically reset itself after impact by pressing a button on control panel, no tools required.

            - Upon bottom edge impact at any position in the closing direction of travel, the fabric curtain stops and reverses direction to the open position.

        - Curtain Jamb Guides:  Side frame assemblies constructed of galvanized steel with extruded aluminum covers.

          - Side frame assemblies shall extend a maximum of 2.21 inches (56.2 mm) from the wall.

          - Side frame assemblies shall have a maximum width of 2.76 inches (70.5 mm) beyond each side of the clear door opening.

          - Inner curtain guide shall be constructed of polyethylene (PE-UHMW 1000); outer section 9/16” x 9/16”.  The inner side guide must form a tight air seal when accommodating the curtain.

          - Door must have no visible air gaps along the side or top of the door when the door panel is in the closed or down position.

          - Side guides shall be free of wearable blade or brush type weather strip systems.

        - Door Header:  Top roll assembly constructed of extruded aluminum drum barrel with press-fit steel axles supported in powder coated steel brackets at each end by self-aligning bearings.

          - Drum Barrel System:  Minimum 4 inches (100 mm) diameter steel.

            - Drum barrel shafts are constructed from nominal 30mm diameter ASTM A663 steel shafts.

          - Top Plates:  Minimum 1/8 inch (3 mm) galvanized steel with heavy-duty, self-aligning bearings to support the drum barrel.

          - Springless System: no balancing springs or counterweights allowed

          - Head frame shall be provided with a 1/8 inch (3mm) galvanized steel sealing profile.

          - Top Roll Cover:  Galvanized steel sheet metal cover spanning the full width of the top roll shall be a minimum 2mm thickness.

        - Electric Door Operator:  Reversible-type motor with controller for motor exposure indicated.

          - Usage Classification:  Heavy duty, rated up to 60 cycles per hour and over 1000 cycles per day.

          - Motor Exposure:  Exterior and Interior use.

          - Side Mounted:  Operator is mounted to the header assembly on the left or right side of door and connected to door drive shaft.

          - Electrical Characteristics:

            - Phase:   Three phase.

            - Volts:    [230-240 Volt.]  [460-480 Volt.]  [575 Volt.]

            - Hertz:  50/60.

          - Operator:   Minimum 1.0 horsepower.

            - The motor and gearbox shall be designed for high cycle operation.

- NOTE:  Contact the factory for amperage draw  –  dependent on door operator voltage and product options.

          - Drive System:  Hollow shaft helical-worm drive.

          - Hand Crank:  Manual brake disengagement lever and hand crank which allows door to be manually opened and closed without electrical power during installation.

          - Limit Switches:  Equip each motorized door with adjustable switches interlocked with motor controls and set to automatically stop door at fully opened and fully closed positions.

          - Timer:  Each door to have automatic closing controlled by an adjustable hold open time delay.

      - CONTROL PANEL

        - MCC VectorControl™ Variable Frequency Control System.

          - Controller housed in a NEMA-4 rated enclosure.

          - Controls must include a frequency vector control drive system capable of infinitely variable speed control in both the up and down directions and integrated programmable capability allowing field customization of logic I/O functionality without adding components.

          - Operational parameters must be set from the Graphical User Interface (GUI).

          - Controller comes with factory set parameters, a 64 bit scrollable graphic/text display that shows functional information during normal operation and will advise if maintenance is required or of abnormal situations.

          - Controls must be fully self-diagnostic thru the GUI and provide corrective actions for error conditions.

          - Control interface must display options and guidance in full text displayed language.  Language options must be available in English, Spanish, French, German, or Portuguese languages.

          - Door must be provided with electronic encoder. A proximity or rotary switch must be provided to accommodate the top position reference.

      - ACTIVATION DEVICES

        - General:  Provide activation devices for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.

- NOTE:  Select activation devices from the options below

        - [Pedestrian Type Activation Devices:]

          - [Single Push Button Switch: Push to open, timer to close.]

          - [Palm Push Button Switch:  Large type push button - push to open, timer to close.]

          - [Three Push Button Switch:  Button for open, button for close, button for stop.]

          - [Pull Cord:  Pull to open - Timer to Close.]

          - [Pull Cord:  Pull to Open – Pull to Close.]

          - [Heated Pull Cord:  For pull cord applications below 32 deg F (0 deg C).  Pull to open - Timer to Close, or Pull to Open – Pull to Close.]

          - [Motion Sensor:  BEA Falcon, microwave scanner, field adjustable wide angle.]

            - Differentiates between pedestrian and vehicular traffic.

            - Prevents false activation from cross traffic,

            - Remote control for set-up.

          - [Presence Sensor:  BEA IRIS, active infrared.]

            - Detects slow moving or non-moving persons or objects.

            - Prevents premature automatic closing of door when pedestrians working near doorway.

            - Remote control for set-up.

        - [Vehicular Type Activation Devices:]

          - [Motion Sensor:  BEA Falcon, microwave scanner, field adjustable wide angle.]

            - Differentiates between pedestrian and vehicular traffic.

            - Prevents false activation from cross traffic,

            - Remote control for set-up.

          - [Loop Detector: Detects ferrous metal objects via an inductive field for activation.  Requires a channel to be cut into floor to install inductive loop wire.]

          - [Pull Cord:  Pull to open - Timer to Close.]

          - [Pull Cord:  Pull to Open – Pull to Close.]

          - [Heated Pull Cord:  For pull cord applications below 32 deg F (0 deg C).  Pull to open - Timer to Close, or Pull to Open – Pull to Close.]

          - [Radio Control Activation:  Near proximity portable push button remote control programmable to individual doors or multiple doors in common.]

            - [One Button Remote Control.]

            - [Four Button Remote Control.]

      - SAFETY DEVICES

        - General:  Provide safety devices for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate safety devices with door operation and door operator mechanisms.

        - Door to be provided with one (1) set of Through Beam Photo Eyes.

        - Door to be provided with failsafe electric safety edge.

          - Connections between the safety edge and controller must be fully wireless. No coil cords allowed.

          - Bottom bar wireless system battery must be able to be replaced at ground level.

      - DOOR FABRIC

- NOTE:  Select color option for door fabric as required – Coordinate with the door fabric specified for the project

        - Door Fabric Material:

          - [Blue 27 oz/yd2 PVC (RAL 5010)]

          - [Orange 27 oz/yd2 PVC (RAL 2004)]

          - [Grey 27 oz/yd2 PVC (RAL 7042)]

          - [White 27 oz/yd2 PVC (RAL 9016)]

          - [Black 27 oz/yd2 PVC (RAL 9017)]

          - [Red 27 oz/yd2 PVC (RAL 3020)]

          - [Yellow 27 oz/yd2 PVC (RAL 1003)]

          - [Greed 27 oz/yd2 PVC (RAL 6028)]

      - FINISH REQUIREMENTS

        - Comply with NAAMM/NOMMA's "Metal Finishes Manual for Architectural and Metal Products (AMP 500-06)" for recommendations for applying and designating finishes.

        - ALUMINUM FINISHES

          - Clear Anodize Finish on Side Frames.

- EXECUTION

      - EXAMINATION

        - Examine substrates areas and conditions, with Installer present, for compliance with requirements for substrate construction and other conditions affecting performance of the Work.

        - Examine locations of electrical connections.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install high performance overhead coiling doors and operating equipment complete with necessary hardware, anchors, inserts, hangers, and equipment supports; according to manufacturer's written instructions and as specified.

        - Install high performance overhead coiling doors, hoods, controls, and operators at the mounting locations indicated for each door.

        - Accessibility:  Install high performance overhead coiling doors, switches, and controls along accessible routes in compliance with regulatory requirements for accessibility.

      - STARTUP SERVICE

        - Engage a factory-authorized service representative to perform startup service.

          - Perform installation and startup checks according to manufacturer's written instructions.

          - Test and adjust controls and safety devices.  Replace damaged and malfunctioning controls and equipment.

      - ADJUSTING

        - Adjust hardware and moving parts to function smoothly so that doors operate easily, free of warp, twist, or distortion.

          - Adjust exterior doors and components to be weather-resistant.

        - Lubricate bearings and sliding parts as recommended by manufacturer.

        - Adjust seals to provide tight fit around entire perimeter.

      - CLEANING AND PROTECTION

        - Clean adjacent surfaces soiled by door installation.

        - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages finish to match original finish.

      - DEMONSTRATION

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain high performance overhead coiling doors.

END OF SECTION 08 33 23.13